- Grease Interceptor Installation Requirement Criteria: Grease interceptors are required for all facilities used 
and operated regularly for the commercial preparation of foods. Businesses requiring grease interceptors 
include, but are not limited to, restaurants, cafes, fast food outlets, pizza outlets, delicatessens, sandwich 
shops, and any other kinds and types of food vending establishments in which any food preparation 
(including heating or defrosting in or by means of any kind of oven or heating device) takes place on the 
premises, whether or not such facilities are located in a separate building or structure or occupied by other 
businesses, as well as schools, churches, boarding houses with communal kitchen facilities, nursing 
homes, and daycare centers which have kitchens and engage in the preparation of food.

If there is more than one building in the facility in which food preparation takes place, each building shall 
have its own grease interceptor sized as outlined in the minimum requirements or all buildings may 
discharge to a single grease interceptor that has been sized to the criteria for each individual kitchen.

The exception shall be those facilities granted a variance, after review and approval from the 
superintendent of the POTW. Grease interceptors shall not be required for private residences or dwellings.

- Grease Interceptor Design Criteria: Each business establishment, for which a grease interceptor is 
required, shall have a dedicated service and grease interceptor. The design of the grease interceptor shall 
be in accordance with the minimum requirements enacted by the village of Fox Lake as indicated below, 
and shall have a minimum of two (2) compartments with fittings designed for grease retention.

Minimum Requirements

1.  Installation of an outside grease interceptor with a minimum liquid holding capacity of one thousand 
(1,000) gallons. (Sandwich bars and carryout services, which only prepare noncooked foods such as cold 
sandwiches, shall install a minimum 400 gallon grease interceptor unless the superintendent of the POTW 
grants a variance.)

2. Installation of a four foot (4') diameter inspection/sampling manhole downstream of grease interceptor.

a. All washroom facilities.

3. All miscellaneous sinks, slop sinks, floor drains, water wash hoods, etc., located in the kitchen area 
shall be plumbed to connect into the new grease interceptor.

4. Prohibited discharge to the grease interceptor includes:

b. Food waste grinders.

c. Dishwashing machines.

There shall be an adequate number of manholes to provide access for the cleaning of all areas of an 
interceptor; a minimum of one per interceptor section, and one sampling manhole directly downstream of 
the interceptor and prior to the effluent entering the sewer main. Manhole covers shall be gastight in

construction and have a minimum opening dimension of twenty four inches (24").

One complete set of plans shall be submitted to the village of Fox Lake building department, these plans 
at a minimum shall include mechanical and plumbing sections. Additionally, the plans shall include size, 
type and location of each interceptor proposed.

The village of Fox Lake building commissioner shall approve these plans including size, type and location

7-3A-19: FATS, OIL AND GREASE DISCHARGE POLICY:

EXHIBIT H

Page 1 of 5

7-3A-19: FATS, OIL AND GREASE DISCHARGE POLICY:

of the interceptor prior to any construction at the proposed site.

Page 2 of 5

C.Grease Interceptor's Location: Each grease interceptor shall be installed and connected such that it is 
easily accessible at all times for inspection, cleaning, and the removal of intercepted grease. the grease 
interceptor(s) shall be located as close to the source as practical, however it must be outside the facility 
served whenever possible. The village of Fox Lake building commissioner prior to any construction on the 
proposed site shall approve the location of any grease interceptor.

D.lnspection Of Grease Interceptors: The village of Fox Lake industrial pretreatment department shall inspect 
all grease interceptors within the village of Fox Lake and develop a mechanism to inventory all grease 
interceptors of properties connected to the collection system, and document the inspections of these 
grease interceptors. Once all the grease interceptors in the service area are identified, the grease 
interceptors shall be classified into two (2) categories:

1. Problem Or Significant Grease Interceptors: The facilities connected to these grease interceptors 
contribute significant amounts of animal/vegetable fats, oil, grease and/or admissible wastes to the 
collection system or facilities which have been defined as a chronic problem facility. These grease 
interceptors shall be inspected and documented at a frequency of once every six (6) months or as 
deemed necessary.

2. Nonsignificant Grease Interceptor: The facilities connected to these grease interceptors do not 
contribute significant amounts of animal/vegetable fats, oil, grease and/or admissible wastes to the 
collection system. These grease interceptors shall be inspected and documented at a frequency of once 
every twelve (12) months or as deemed necessary.

E.Grease Interceptor Maintenance And Pumping Schedules:

1. It shall be the responsibility of the owner to assure that proper maintenance and pumping/cleaning of 
the grease interceptor is properly performed and documented. All grease interceptors shall be maintained 
in efficient operating condition. When pumping/cleaning of the grease interceptor is performed the entire 
contents of the grease interceptor shall be removed, which includes the removal of all accumulated 
grease, solids and liquid. The pumping/cleaning of the grease interceptor shall be performed in 
accordance with the schedule listed below and shall be performed in a manner that does not discharge 
grease into the collection system. At no time may any portion of the contents removed from the grease 
interceptor be discharged back into the grease interceptor or the sanitary sewer system. The ownerllessee 
shall conduct, on a monthly basis, an inspection of each interceptor. At no time may the accumulated 
grease and/or solids exceed twenty five percent (25%) of the holding capacity of the grease interceptor. 
These inspections and cleanings must be documented and the records kept on site for a minimum of two 
(2) years. Records to be kept on site shall include a maintenance log showing each date of pumping or 
service and copies of receipts and manifests describing each pumping or service. All records shall be 
made available to the pretreatment inspector (upon request). All grease and/or solids removed from the 
grease interceptor must be properly documented and disposed of by a licensed waste hauler.

2. All existing business/industrial users connected to grease interceptors prior to the implementation of this 
fats, oil and grease discharge policy are required to pump and clean their interceptor(s) at a minimum 
frequency of once every thirty (30) days. Inspections and samplings of grease interceptor(s) by the village 
of Fox Lake pretreatment department shall determine if this pumping/cleaning frequency is adequate to 
control the amounts of fats, oils, grease and/or admissible wastes entering the collection system or if the 
pumping/cleaning frequency needs to be adjusted. The village of Fox Lake pretreatment department has 
the right to increase the pumping and cleaning frequency as deemed necessary. All requests to reduce

the pumping/cleaning frequency must be submitted to the village of Fox Lake pretreatment department, in 
letter form. The address is:

7-3A-19: FATS, OIL AND GREASE DISCHARGE POLICY:

Village of Fox Lake NWRWRF

Page 3 of 5

Pretreatment Department

200 Industrial Avenue

Fox Lake, IL 60020

The village of Fox Lake pretreatment department must approve any changes to this frequency in writing 
prior to any change being made. In addition, the village of Fox Lake pretreatment department may require 
the business/industrial user to implement best management practices in order to reduce its discharge to 
acceptable levels.

3. All new, remodeled and/or chronic problem facilities required to connect to a grease interceptor(s) in 
accordance with the provision of this policy are required to pump and clean their interceptor(s) once every 
sixty (60) days (or every other month). Inspections and samplings of grease interceptor(s) by the village of 
Fox Lake pretreatment department shall determine if this pumping/cleaning frequency is adequate to 
control the amounts of fats, oils, grease and admissible wastes entering the collection system or if the 
pumping/cleaning frequency needs to be adjusted. The village of Fox Lake pretreatment department has 
the right to increase the pumping and cleaning frequency as deemed necessary. All requests to reduce 
the pumping/cleaning frequency must be submitted to the village of Fox Lake pretreatment department, in 
letter form. The address is:

Village of Fox Lake NWRWRF

Pretreatment Department

200 Industrial Avenue

Fox Lake, IL 60020

The village of Fox Lake pretreatment department must approve any changes to this frequency in writing 
prior to any changes being made.

4. If deficiencies are found during an inspection performed by the village of Fox Lake, the owner shall 
have three (3) weeks to bring the facility into compliance. If the grease interceptor fails a second 
(consecutive) inspection, the village of Fox Lake shall require the owner to contract with a qualified 
contractor to install new or additional equipment to bring the facility into compliance. This work shall be 
completed within six (6) months of the date the village requires such contract to be made. The cost of all 
work required to bring the facility into compliance shall be the burden of the owner.

F.Biological Treatment: Biological treatment shall not be a substitute for the complete pumping of the grease 
interceptor at the frequency described in this policy.

G.Existing Sources Not Connected To Grease Interceptors: Existing sources offats, oil, grease and/or 
admissible wastes not connected to grease interceptors, which contribute significant amounts of fats, oil, 
grease and/or admissible wastes will be identified through inspection of the collection system by the 
village of Fox Lake sewer department. Once these sources are identified, the sewer department shall 
notify the pretreatment department of their presence. The pretreatment department shall in writing require 
these facilities to implement best management practices (BMPs) to keep fats, oil, grease and excessive 
amounts of admissible waste out of the wastewater collection system. All BMPs must be submitted to the 
pretreatment department for review and approval. Examples of a BMP include:

Violation

Noncompliance with local limits 
on discharge (section 7-3A-13 
of this article)

Noncompliance with local limits 
on discharge, second violation 
in a six (6) month period 
Noncompliance with local limits 
on discharge, more than two (2) 
violations in a six (6) month 
period

Fine 
$150.00

250.00

750.00 per violation (in 
addition to further 
legal actions)

Page 4 of 5

If the sewer department finds through inspections of the collection system that the implemented BMPs are 
not successful at the facility and the facility continues to contribute significant amounts of fats, oil, grease 
and/or admissible wastes to the collection system, the owner will be required to install an adequately sized 
grease interceptor as outlined in this policy within six (6) months after being notified.

7-3A-19: FATS, OIL AND GREASE DISCHARGE POLICY: 
1. Scrape food from plates into garbage cans.

2. Prewash plates by spraying them off with cold water over a small mesh catch basin positioned over a 
drain. This catch basin should be cleaned into a garbage can as needed.

3. Pour all liquid oil and grease from pots and pans into a waste grease bucket stored at the pot washing 
sink. Heavy solids buildup of oil and grease on pots and pans should be scraped off into waste grease 
bucket.

4. Other kitchen practices identified by the village of Fox Lake or the facility, connector communities or 
sanitation district and/or facility which will decrease the point source discharge of fats, oil, grease and/or 
admissible wastes.

H.Request For Variance: If a facility that is required to install a grease interceptor finds and documents by a 
licensed plumber that the facility cannot meet the minimum requirements for a grease interceptor, that 
facility may submit in writing a variance request. This request must explain the situation, which makes the 
minimum requirement unachievable, along with an alternative plan for FOG and/or admissible waste 
reduction. This request must be submitted to the village of Fox Lake pretreatment department within thirty 
(30) days of the order to install a grease interceptor.

If a facility believes that the pumping/cleaning schedule should be decreased the facility must submit in 
writing a variance request. This request must include a statement from the grease removal company that 
the facility has pump/clean their interceptor. The request must also state the frequency the facility feels 
would be adequate.

No changes to any portion of the FOG policy can be changed until the facility receives from the POTW a 
written letter either accepting, accepting with conditions or denying the variance request. The facility must 
abide by the terms the POTW specifies.

I.Penalties And Fees: The penalties, fines and/or fees associated with noncompliance with this fats, oil and 
grease discharge policy or portions of the pretreatment ordinance shall be as follows:

7-3A-19: FATS, OIL AND GREASE DISCHARGE POLICY:				    	         Page 5 of 5

Noncompliance with pumping/	250.00
cleaning schedule

Noncompliance with pumping/	75.00 per violation
cleaning schedule more than

once in one year

Noncompliance with record keeping	250.00 per violation

or reporting requirements

Any sanitary sewer overflow (SSO) 	75.00 per violation

Any sewer backup 		500.00 per violation

The fees associated with the FOG policy are as follows:

Activity 		Fee

Any facility that requires the 		$150.00 per inspection

to install a grease interceptor 
in accordance with this policy 
shall need an inspection by 
the village plumbing inspector.

All fines, fees and compliance orders must be paid in full or satisfied before any new or renewal of 
business license application will be approved. The village has the right to revoke any business license for a facility (within Fox Lake), which has an outstanding balance or an unresolved compliance order.

If business license renewal occurs within a compliance schedule a temporary license may be issued until the final compliance date.

Compliance status shall be reviewed annually, at the time of business license renewal. All fines, fees and compliance orders must be paid in full or satisfied before applications will be approved. No license shall be issued to a facility with an outstanding balance.

The above penalties, fines and/or fees may be assessed by the supervisor of the POTW. If a person or company against whom a penalty, fine or fee is assessed under this FOG discharge policy disputes the assessment of the penalty, fine or fee and notifies the POTW in writing of the basis for the dispute within thirty (30) days after assessment of the penalty, fine or fee, then the supervisor of the POTW may adjust the penalty, fine or fee if sufficient cause exists to do so. If the supervisor of the POTW does not believe the penalty, fine or fee should be adjusted, then he shall deliver copies of the original assessment notice and the notice of dispute to the chairman of the sewer and water committee of the village board within fourteen (14) days after the notice of dispute. The sewer and water committee shall thereafter schedule a public hearing before the sewer and water committee, or its designee, which hearing shall be scheduled for no later than thirty (30) days after the notice of dispute has been received by the chairman of the sewer and water committee. The person or company against whom the penalty, fine or fee has been assessed shall be given at least fourteen (14) days' written notice of the hearing. The purpose of the hearing shall be to review the decision of the supervisor of the POTW assessing the penalty, fine or fee, and the decision of a majority of the sewer and water committee shall be final. (Ord. 2005-10, 3-15-2005)